## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-05-2025 | during | 12-05-2025 | during | 12-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 364 | 341 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 351 | 351 | Allocation limit by Titas Gas
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 292 | 290 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 50 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 268 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 0 | 8 | 102 | 8 | 102
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 78 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 17.5 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 30 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 108 | 112 | 135 | 135 | 135 | 135 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 10 | 67 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 90 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 300 | 584 | 584 | 300 | 300 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 250 | 250 | 583 | 583 | 250 | 250 | Allocation limit by Titas Gas
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 52 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2568 | 2488.5 | 5257.9 | 5319.9 | 3294.62 | 3356.62
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 20 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 141 | 148 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 5 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 16 | 76 | 72 | 72 | 56 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 100 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 87 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 0 | 8 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 16 | 108 | 108 | 70 | 70 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.41 | 0 | 4.41 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 1 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 36 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 143 | 143 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1150 | 1224 | 612 | 612 | 1224 | 1224 | machine problem
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 2 | 7 | 2 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 505 | 557 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2104 | 2333 | 2785.27 | 2785.86 | 3360.13 | 3384.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 207 | 180 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 220 | 250 | 235 | 235 | 235 | 235 | ST Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 345 | 345 | 345 | 345 | 345 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 29 | 33 | 46.94 | 46.94 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 53 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 73 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 45 | 30 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 27 | 31 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 170 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 18 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 39 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 90 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1624.2 | 1599 | 2355.64 | 2287.64 | 2134.2 | 2095.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-05-2025 | during | 12-05-2025 | during | 12-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 157.5 | 157.5 | 22 | 22 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 165 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 64 | 96 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 248 | 301 | 599.1 | 549 | 331.6 | 353.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 38 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 134 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 28 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 323 | 356 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1146 | 1151 | 1293 | 1293 | 1200 | 1200
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 922 | 926 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 222 | 212 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 52 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94.63 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1082 | 1220 | 617.1 | 617.1 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2320.63 | 2410 | 2990.1 | 2895.1 | 3394.01 | 3299.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 310 | 345 | 620 | 620 | 620 | 620 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 9 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 105 | 105 | 125 | 125 | 113 | 113 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1039 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.67 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1933.67 | 2248 | 2787.12 | 2786.12 | 2735.12 | 2734.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 3 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 202 | 206 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 197 | 200 | 220 | 220 | 220 | 220
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 360 | 370 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 3 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.42 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1362.57 | 1449 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.74 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 2281.73 | 2228 | 3180.87 | 3014.87 | 2922.08 | 2756.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 51 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 164 | 165 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.5 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 188 | 0 | 178.95 | 0 | 178.95 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 510.5 | 286 | 687.55 | 472 | 687.55 | 472
System Total |  |  |  |  | 27566.2 | 28624.082 | 14736.73 | 15044.5 | 21936.55 | 21403.49 | 20059.31 | 19651.25
Forecast Scenario (12-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15320 |  | 0 |  | 15320
|  |  |  | 1:00 | 14750 |  | 0 |  | 14750
|  |  |  | 2:00 | 14200 |  | 0 |  | 14200
|  |  |  | 3:00 | 13590 |  | 0 |  | 13590
|  |  |  | 4:00 | 13200 |  | 0 |  | 13200
|  |  |  | 5:00 | 12990 |  | 0 |  | 12990
|  |  |  | 6:00 | 12470 |  | 0 |  | 12470
|  |  |  | 7:00 | 12490 |  | 0 |  | 12490
|  |  |  | 8:00 | 12340 |  | 0 |  | 12340
|  |  |  | 9:00 | 12760 |  | 0 |  | 12760
|  |  |  | 10:00 | 13270 |  | 0 |  | 13270
|  |  |  | 11:00 | 13820 |  | 0 |  | 13820
|  |  |  | 12:00 | 14390 |  | 0 |  | 14390
|  |  |  | 13:00 | 14680 |  | 0 |  | 14680
|  |  |  | 14:00 | 14710 |  | 0 |  | 14710
|  |  |  | 15:00 | 14720 |  | 0 |  | 14720
|  |  |  | 16:00 | 14480 |  | 0 |  | 14480
|  |  |  | 17:00 | 14170 |  | 0 |  | 14170
|  |  |  | 18:00 | 13720 |  | 0 |  | 13720
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15260 |  | 0 |  | 15260
|  |  |  | 19:30 | 15500 |  | 0 |  | 15500
|  |  |  | 20:00 | 15500 |  | 0 |  | 15500
|  |  |  | 21:00 | 15670 |  | 0 |  | 15670
|  |  |  | 22:00 | 15650 |  | 0 |  | 15650
|  |  |  | 23:00 | 15550 |  | 0 |  | 15550
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 14390.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15670.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15670.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 339.70 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:14 hrs on 12-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-05-2025 | [28 empty] | Date: | 11-05-2025 | [28 empty] | Date: | 11-05-2025 | [28 empty] | Date: | 11-05-2025 | [28 empty] | Date: | 11-05-2025 | [16 empty] | Date: | 11-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 17 | 17 | 131 | 127 | 294 | 55 | 0 | 90 | 0 | 16 | 300 | 299 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 160 | 9 | 22 | 0 | 300 | 61 | 65 | 56 | 0 | 0 | 102 | 53 | 54 | 100 | 88 | 0 | 40 | 110 | 12 | 552 | 160 | 0 | 50 | 25 | 87 | 146 | 0 | 0 | 0 | 1226 | 0 | 51 | 135 | 180 | 0 | 0 | 345 | 52 | 214 | 36 | 51 | 70 | 108 | 18 | 20 | 114 | 52 | 52.2 | 0 | 37 | 320 | 0 | 331 | 36 | 30 | 0 | 153 | 8 | 0 | 80 | 20 | 0 | 16 | 170 | 17 | 47 | 137 | 22 | 0 | 0 | 12 | 8779.2 | 780 | 262 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1023 | 17 | 1363.96 | 0 | 46 | 0 | 113 | 17 | 93 | 113 | 36 | 42 | 0 | 0 | 0 | 200 | 0 | 197 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 170 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 10 | 115 | 220 | 0 | 452 | 1244 | 0 | 7584.96 | 16364.16 | 78.18
01:00 | 8 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17 | 17 | 130 | 112 | 294 | 55 | 0 | 54 | 0 | 16 | 350 | 292 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 0 | 160 | 9 | 22 | 0 | 300 | 72 | 65 | 57 | 0 | 0 | 102 | 53 | 54 | 100 | 88 | 0 | 40 | 110 | 12 | 550 | 160 | 0 | 50 | 25.5 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 180 | 0 | 0 | 345 | 51 | 215 | 36 | 50 | 50 | 106 | 9 | 20 | 114 | 52 | 52.2 | 0 | 37 | 310 | 0 | 322 | 36 | 30 | 0 | 150 | 8 | 0 | 80 | 25 | 0 | 16 | 170 | 0 | 47 | 91 | 22 | 0 | 0 | 12 | 8606.7 | 921 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 17 | 1353.26 | 0 | 46 | 0 | 113 | 17 | 92 | 113 | 0 | 42 | 0 | 0 | 0 | 200 | 0 | 193 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 170 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 105 | 220 | 0 | 452 | 1244 | 0 | 7486.26 | 16092.96 | 78.17
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 130 | 80 | 294 | 55 | 0 | 54 | 0 | 16 | 350 | 292 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 0 | 72 | 8.5 | 22 | 0 | 300 | 72 | 65 | 31 | 0 | 0 | 93 | 53 | 54 | 100 | 88 | 0 | 40 | 110 | 16 | 552 | 124 | 0 | 50 | 25.5 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 180 | 0 | 0 | 345 | 51 | 215 | 35 | 57 | 50 | 108 | 9 | 20 | 114 | 50 | 52.2 | 0 | 37 | 305 | 0 | 327 | 36 | 30 | 0 | 147 | 8 | 0 | 80 | 28 | 0 | 16 | 170 | 0 | 47 | 91 | 22 | 0 | 0 | 12 | 8384.2 | 923 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 17 | 1362.17 | 0 | 46 | 0 | 113 | 17 | 0 | 113 | 16 | 42 | 0 | 0 | 0 | 199 | 0 | 192 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 168 | 52 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 115 | 220 | 0 | 452 | 1244 | 0 | 7463.17 | 15847.37 | 78.16
03:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 119 | 80 | 245 | 55 | 0 | 54 | 0 | 16 | 350 | 293 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 0 | 52 | 8.5 | 22 | 0 | 300 | 101 | 135 | 24 | 0 | 0 | 95 | 53 | 17 | 100 | 88 | 0 | 40 | 110 | 28 | 552 | 160 | 0 | 50 | 25.5 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 180 | 0 | 0 | 345 | 52 | 216 | 35 | 68 | 50 | 105 | 8 | 20 | 114 | 48 | 52.2 | 0 | 37 | 300 | 0 | 321 | 36 | 30 | 0 | 147 | 8 | 0 | 80 | 28 | 0 | 16 | 169 | 0 | 47 | 92 | 22 | 0 | 0 | 12 | 8404.2 | 923 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 17 | 1358.72 | 0 | 47 | 0 | 113 | 12 | 0 | 113 | 16 | 18 | 0 | 0 | 0 | 200 | 0 | 192 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 170 | 52 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 11 | 115 | 220 | 0 | 452 | 1244 | 48 | 7088.72 | 15492.92 | 78.15
04:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 113 | 82 | 195 | 55 | 0 | 54 | 0 | 16 | 350 | 288 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 0 | 52 | 8.5 | 22 | 0 | 300 | 110 | 100 | 0 | 0 | 0 | 94 | 53 | 0 | 100 | 88 | 0 | 40 | 110 | 28 | 555 | 124 | 0 | 19 | 0 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 180 | 0 | 0 | 345 | 53 | 217 | 35 | 69 | 50 | 103 | 9 | 20 | 114 | 48 | 52.2 | 0 | 31 | 310 | 0 | 312 | 36 | 30 | 0 | 147 | 8 | 0 | 80 | 28 | 0 | 16 | 169 | 0 | 47 | 92 | 22 | 0 | 0 | 12 | 8178.7 | 922 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 17 | 1359.42 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 188 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 170 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 10 | 110 | 220 | 0 | 452 | 1244 | 100 | 6925.42 | 15104.12 | 78.14
05:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 113 | 82 | 145 | 40 | 0 | 54 | 0 | 16 | 330 | 289 | 250 | 0 | 35 | 0 | 277 | 0 | 0 | 0 | 52 | 8.5 | 22 | 0 | 300 | 35 | 15 | 0 | 0 | 0 | 102 | 53 | 0 | 100 | 88 | 0 | 40 | 110 | 30 | 556 | 0 | 0 | 0 | 0 | 85 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 180 | 0 | 232 | 345 | 53 | 189 | 35 | 69 | 50 | 103 | 9 | 20 | 114 | 44 | 52.2 | 0 | 38 | 300 | 0 | 312 | 36 | 30 | 0 | 145 | 8 | 0 | 80 | 28 | 0 | 16 | 169 | 0 | 47 | 93 | 22 | 0 | 0 | 12 | 8013.7 | 922 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 17 | 1362.76 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 180 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 171 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 110 | 220 | 0 | 452 | 1244 | 100 | 6872.76 | 14886.46 | 78.13
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17 | 17 | 113 | 82 | 0 | 0 | 0 | 54 | 0 | 16 | 300 | 273 | 250 | 0 | 17 | 0 | 266 | 0 | 0 | 2 | 52 | 0 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 23 | 0 | 100 | 50 | 0 | 40 | 110 | 33 | 556 | 0 | 0 | 0 | 0 | 68 | 150 | 0 | 0 | 0 | 1224 | 1 | 51 | 100 | 180 | 0 | 180 | 345 | 53 | 182 | 35 | 53 | 70 | 104 | 9 | 20 | 98 | 42 | 25 | 5 | 38 | 295 | 0 | 312 | 36 | 30 | 0 | 130 | 0 | 0 | 81 | 30 | 0 | 16 | 169 | 0 | 47 | 102 | 22 | 0 | 2.62 | 12 | 7384.62 | 922 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 610 | 17 | 1379.08 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.97 | 201 | 0 | 181 | 0 | 0 | 0 | 320 | 0 | 0.13 | 0 | 169 | 49 | 35 | 1 | 69 | 0 | 0 | 0.3 | 7 | 0.03 | 0 | 307 | 10 | 100 | 180 | 0 | 453 | 1244 | 17 | 6610.91 | 13995.53 | 78.12
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 112 | 82 | 0 | 0 | 0 | 35 | 0 | 0 | 300 | 279 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 7 | 52 | 18 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 34 | 506 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1150 | 4 | 51 | 60 | 180 | 0 | 234 | 300 | 53 | 173 | 35 | 51 | 50 | 103 | 8 | 20 | 98 | 40 | 0 | 17 | 38 | 305 | 0 | 312 | 36 | 30 | 0 | 137 | 0 | 0 | 81 | 70 | 0 | 16 | 169 | 0 | 65 | 120 | 22 | 0 | 9.82 | 12 | 6971.82 | 922 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.15 | 877 | 0 | 1384.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10.67 | 193 | 0 | 172 | 0 | 0 | 0 | 369 | 0 | 0.77 | 0 | 162 | 49 | 35 | 6 | 34 | 0 | 0 | 1.5 | 43 | 0.15 | 0 | 250 | 10 | 100 | 220 | 0 | 453 | 1200 | 0 | 6767.51 | 13739.33 | 78.11
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 88 | 82 | 0 | 0 | 4 | 35 | 0 | 0 | 300 | 293 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 13 | 52 | 23 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 12 | 2 | 40 | 0 | 9 | 453 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1102 | 10 | 51 | 10 | 45 | 0 | 228 | 345 | 5 | 211 | 35 | 50 | 70 | 104 | 8 | 20 | 98 | 38 | 13 | 34 | 38 | 295 | 0 | 335 | 36 | 30 | 0 | 148 | 0 | 0 | 80 | 30 | 0 | 16 | 169 | 0 | 66 | 120 | 18 | 1 | 14.61 | 12 | 6721.61 | 876 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.35 | 1085 | 0 | 1325.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 23.12 | 207 | 0 | 198 | 0 | 0 | 0 | 383 | 0 | 1.71 | 0 | 164 | 51 | 35 | 14 | 34 | 0 | 0 | 2.4 | 84 | 0.32 | 0 | 250 | 7 | 100 | 220 | 0 | 373 | 1100 | 0 | 6874.56 | 13596.17 | 78.1
09:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 89 | 82 | 0 | 0 | 35 | 35 | 0 | 0 | 300 | 296 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 20 | 52 | 22 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 74 | 22 | 3 | 40 | 0 | 4 | 453 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1102 | 17 | 51 | 0 | 45 | 0 | 224 | 345 | 5 | 210 | 35 | 68 | 70 | 121 | 9 | 20 | 98 | 28 | 52.2 | 48 | 37 | 300 | 0 | 325 | 36 | 30 | 0 | 151 | 0 | 0 | 78 | 30 | 0 | 17 | 171 | 0 | 66 | 118 | 18 | 1 | 31.82 | 12 | 6885.02 | 876 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.88 | 1127 | 0 | 1316.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 29.99 | 206 | 0 | 202 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 167 | 52 | 35 | 21 | 34 | 0 | 0 | 4.9 | 124 | 0.49 | 0 | 250 | 9 | 105 | 220 | 0 | 283 | 1098 | 0 | 6929.87 | 13814.89 | 78.09
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 2 | 17 | 110 | 81 | 45 | 1 | 35 | 86 | 0 | 0 | 300 | 292 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 27 | 52 | 22 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 87 | 44 | 4 | 40 | 0 | 5 | 452 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 1100 | 14 | 51 | 0 | 45 | 0 | 221 | 340 | 7 | 208 | 35 | 68 | 70 | 169 | 8 | 20 | 114 | 34 | 52.2 | 58 | 28 | 300 | 0 | 350 | 38 | 30 | 0 | 149 | 0 | 0 | 77 | 30 | 0 | 17 | 172 | 0 | 64 | 116 | 16 | 1 | 38.52 | 12 | 7124.72 | 923 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.63 | 1072 | 0 | 1253.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 32.34 | 204 | 0 | 200 | 0 | 0 | 0 | 351 | 0 | 1.97 | 0 | 162 | 51 | 35 | 28 | 34 | 0 | 0 | 6.4 | 161 | 0.58 | 0 | 250 | 9 | 115 | 220 | 0 | 262 | 1050 | 0 | 6834.83 | 13959.55 | 78.08
11:00 | 4 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17 | 17 | 112 | 78 | 145 | 16 | 35 | 90 | 0 | 0 | 300 | 285 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 24 | 52 | 21 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 87 | 80 | 4 | 40 | 0 | 5 | 500 | 0 | 0 | 0 | 1 | 0 | 140 | 0 | 0 | 0 | 1100 | 13 | 51 | 2 | 65 | 0 | 209 | 330 | 24 | 204 | 31 | 69 | 50 | 200 | 8 | 19 | 114 | 32 | 52.2 | 59 | 28 | 320 | 0 | 351 | 36 | 30 | 0 | 155 | 0 | 0 | 79 | 28 | 0 | 17 | 174 | 0 | 64 | 117 | 10 | 2 | 35.37 | 12 | 7398.57 | 923 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.66 | 1066 | 0 | 1266.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 49.2 | 203 | 0 | 197 | 0 | 0 | 0 | 400 | 0 | 4.13 | 0 | 165 | 51 | 35 | 32 | 34 | 0 | 0 | 7.2 | 178 | 0.66 | 0 | 250 | 9 | 115 | 220 | 0 | 310 | 1045 | 0 | 6983.4 | 14381.97 | 78.07
12:00 | 8 | 34 | 30 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 17 | 108 | 78 | 195 | 50 | 35 | 90 | 0 | 10 | 300 | 292 | 250 | 0 | 17 | 0 | 250 | 0 | 0 | 30 | 52 | 21 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 1 | 17 | 16 | 0 | 87 | 88 | 4 | 40 | 1 | 0 | 505 | 0 | 0 | 24 | 8 | 5 | 141 | 0 | 0 | 0 | 1150 | 17 | 51 | 45 | 63 | 0 | 220 | 335 | 30 | 207 | 29 | 69 | 50 | 200 | 8 | 19 | 114 | 38 | 52.2 | 67 | 27 | 310 | 0 | 323 | 36 | 30 | 0 | 152 | 0 | 0 | 78 | 28 | 0 | 16 | 173 | 0 | 64 | 115 | 10 | 2 | 45 | 12 | 7690.2 | 922 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.63 | 1082 | 0 | 1362.57 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 50.74 | 202 | 0 | 197 | 0 | 0 | 0 | 360 | 0 | 4.42 | 0 | 164 | 50 | 35 | 32 | 34 | 0 | 0 | 7.5 | 188 | 0.67 | 0 | 250 | 9 | 105 | 220 | 0 | 310 | 1039 | 0 | 7046.53 | 14736.73 | 78.06
13:00 | 16 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17 | 17 | 103 | 75 | 195 | 55 | 35 | 90 | 0 | 22 | 300 | 288 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 28 | 90 | 20.5 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 87 | 88 | 3 | 40 | 18 | 0 | 505 | 53 | 0 | 50 | 8 | 19 | 137 | 0 | 0 | 0 | 1150 | 16 | 51 | 88 | 90 | 0 | 208 | 325 | 30 | 204 | 28 | 69 | 50 | 200 | 8 | 19 | 114 | 48 | 52.2 | 64 | 26 | 315 | 0 | 350 | 36 | 30 | 0 | 152 | 8 | 0 | 78 | 25 | 0 | 16 | 173 | 17 | 64 | 102 | 5 | 2 | 40.81 | 7 | 7981.51 | 922 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.96 | 1110 | 7 | 1357.8 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 49.91 | 198 | 0 | 194 | 0 | 0 | 0 | 396 | 0 | 4.13 | 0 | 164 | 51 | 65 | 31 | 40 | 0 | 0 | 6.8 | 178 | 0.61 | 0 | 250 | 9 | 115 | 220 | 0 | 310 | 1047 | 0 | 7177.21 | 15158.72 | 78.05
14:00 | 16 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 15 | 89 | 75 | 195 | 55 | 35 | 90 | 0 | 41 | 300 | 278 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 25 | 90 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 16 | 38 | 0 | 87 | 100 | 1 | 40 | 34 | 2 | 505 | 143 | 0 | 50 | 9 | 34 | 140 | 0 | 0 | 0 | 1150 | 15 | 51 | 95 | 90 | 0 | 219 | 335 | 37 | 204 | 29 | 69 | 50 | 200 | 8 | 19 | 114 | 44 | 43 | 55 | 26 | 310 | 0 | 333 | 38 | 30 | 0 | 152 | 8 | 0 | 77 | 28 | 0 | 16 | 173 | 17 | 73 | 102 | 5 | 2 | 35.17 | 12 | 8116.17 | 924 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8 | 1158 | 17 | 1362.17 | 0 | 0 | 0 | 107 | 0 | 0 | 100 | 0 | 16 | 89 | 0 | 43.34 | 198 | 0 | 191 | 0 | 0 | 0 | 354 | 0 | 3.81 | 0 | 163 | 50 | 112 | 27 | 97 | 0 | 0 | 4.7 | 158 | 0.56 | 0 | 270 | 10 | 105 | 220 | 0 | 311 | 1052 | 0 | 7439.38 | 15555.55 | 78.04
15:00 | 16 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17 | 16 | 95 | 75 | 195 | 55 | 35 | 90 | 0 | 50 | 300 | 285 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 20 | 90 | 19 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 16 | 39 | 0 | 87 | 100 | 1 | 37 | 34 | 2 | 505 | 160 | 0 | 50 | 22 | 34 | 140 | 0 | 0 | 0 | 1150 | 12 | 51 | 90 | 128 | 0 | 220 | 335 | 41 | 190 | 29 | 69 | 50 | 200 | 12 | 16 | 114 | 50 | 52.2 | 43 | 26 | 310 | 0 | 319 | 35 | 30 | 0 | 151 | 8 | 0 | 77 | 30 | 0 | 16 | 172 | 17 | 72 | 92 | 5 | 2 | 0.24 | 12 | 8139.44 | 923 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.44 | 1158 | 17 | 1366.57 | 0 | 0 | 0 | 110 | 0 | 0 | 113 | 0 | 16 | 72 | 0 | 33.97 | 198 | 0 | 192 | 0 | 0 | 0 | 360 | 0 | 3.07 | 0 | 164 | 48 | 110 | 21 | 100 | 0 | 0 | 2 | 112 | 0.44 | 0 | 270 | 10 | 105 | 220 | 0 | 311 | 1000 | 0 | 7303.49 | 15442.93 | 78.03
16:00 | 32 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 16 | 98 | 75 | 145 | 55 | 35 | 90 | 0 | 50 | 300 | 280 | 250 | 0 | 35 | 0 | 250 | 0 | 0 | 13 | 28 | 18 | 20 | 0 | 300 | 0 | 0 | 24 | 0 | 9 | 16 | 47 | 0 | 88 | 100 | 2 | 39 | 34 | 0 | 500 | 108 | 0 | 50 | 25.5 | 17 | 141 | 0 | 0 | 0 | 1150 | 7 | 51 | 102 | 150 | 0 | 251 | 345 | 46 | 178 | 30 | 69 | 50 | 191 | 25 | 16 | 114 | 48 | 52.2 | 26 | 26 | 300 | 0 | 313 | 35 | 30 | 0 | 137 | 8 | 0 | 78 | 30 | 0 | 16 | 172 | 0 | 74 | 101 | 10 | 1 | 1.9 | 12 | 7974.6 | 922 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.21 | 1102 | 17 | 1387.4 | 0 | 0 | 0 | 110 | 4 | 60 | 10 | 0 | 8 | 50 | 0 | 22.02 | 198 | 0 | 190 | 0 | 0 | 0 | 320 | 0 | 1.98 | 0 | 164 | 51 | 95 | 13 | 107 | 0 | 0 | 0.6 | 80 | 0.31 | 0 | 220 | 9 | 105 | 220 | 0 | 268 | 900 | 0 | 6881.52 | 14856.12 | 78.02
17:00 | 50 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 16 | 102 | 75 | 145 | 55 | 35 | 90 | 0 | 53 | 300 | 278 | 250 | 0 | 35 | 0 | 260 | 0 | 0 | 6 | 17 | 17 | 20 | 0 | 300 | 0 | 0 | 61 | 0 | 4 | 92 | 45 | 0 | 100 | 70 | 0 | 40 | 0 | 0 | 455 | 17 | 0 | 50 | 25.5 | 0 | 142 | 0 | 0 | 0 | 1062 | 3 | 51 | 128 | 73 | 0 | 180 | 300 | 46 | 218 | 31 | 69 | 50 | 180 | 35 | 14 | 114 | 42 | 52.2 | 12 | 26 | 290 | 0 | 312 | 35 | 30 | 0 | 129 | 8 | 0 | 78 | 30 | 0 | 16 | 172 | 0 | 74 | 110 | 11 | 1 | 0.12 | 12 | 7635.82 | 922 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.22 | 1001 | 17 | 1435.59 | 0 | 0 | 0 | 35 | 5 | 60 | 0 | 0 | 8 | 13 | 0 | 10.41 | 140 | 0 | 140 | 0 | 0 | 0 | 319 | 0 | 0.93 | 0 | 160 | 50 | 35 | 6 | 50 | 0 | 0 | 0 | 34 | 0.14 | 0 | 159 | 8 | 105 | 180 | 0 | 300 | 890 | 0 | 6310.29 | 13946.11 | 78.01
18:00 | 0 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 28 | 10 | 110 | 80 | 80 | 55 | 35 | 90 | 0 | 62 | 300 | 253 | 250 | 0 | 35 | 0 | 260 | 0 | 0 | 2 | 0 | 18 | 18 | 0 | 300 | 0 | 0 | 64 | 0 | 1 | 96 | 54 | 0 | 100 | 38 | 0 | 40 | 0 | 0 | 406 | 0 | 0 | 50 | 25.5 | 0 | 145 | 0 | 0 | 0 | 900 | 0.41 | 5 | 60 | 8 | 0 | 130 | 250 | 21 | 180 | 32 | 75 | 50 | 176 | 36 | 0 | 114 | 28 | 8 | 2 | 29 | 280 | 0 | 338 | 36 | 30 | 0 | 127 | 0 | 0 | 21 | 30 | 0 | 16 | 173 | 0 | 16 | 45 | 11 | 0 | 0 | 12 | 6656.91 | 921 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.23 | 928 | 17 | 1445.42 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 21 | 8 | 2 | 0 | 1.13 | 140 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 0.11 | 0 | 163 | 50 | 35 | 0 | 50 | 0 | 0 | 0 | 7 | 0.03 | 0 | 150 | 9 | 90 | 180 | 0 | 300 | 850 | 0 | 6110.92 | 12767.83 | 78
19:00 | 16 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 50 | 9 | 111 | 62 | 80 | 55 | 35 | 90 | 0 | 67 | 300 | 296 | 250 | 0 | 35 | 0 | 277 | 0 | 0 | 0 | 0 | 18.4 | 21 | 0 | 300 | 0 | 0 | 63 | 0 | 0 | 101 | 66 | 0 | 100 | 70 | 0 | 40 | 0 | 7 | 540 | 0 | 0 | 50 | 25.5 | 0 | 143 | 0 | 0 | 0 | 1045 | 0 | 28 | 75 | 36 | 0 | 194 | 345 | 12 | 191 | 30 | 90 | 50 | 178 | 36 | 6 | 114 | 40 | 16 | 0 | 30 | 300 | 0 | 345 | 36 | 30 | 0 | 141 | 0 | 0 | 78 | 30 | 0 | 16 | 172 | 0 | 19 | 37 | 11 | 0 | 0 | 12 | 7445.9 | 879 | 220 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 956 | 17 | 1455.04 | 0 | 0 | 0 | 0 | 11 | 62 | 0 | 36 | 8 | 0 | 0 | 0 | 145 | 0 | 187 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 163 | 48 | 51 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 228 | 11 | 105 | 220 | 0 | 325 | 860 | 17 | 6495.04 | 13940.94 | 77.99
19:30 | 16 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 111 | 87 | 145 | 15 | 35 | 90 | 0 | 67 | 300 | 256 | 250 | 0 | 35 | 0 | 265 | 0 | 0 | 0 | 28 | 18 | 22 | 0 | 300 | 0 | 0 | 65 | 0 | 0 | 101 | 70 | 0 | 100 | 70 | 0 | 40 | 0 | 3 | 553 | 0 | 0 | 50 | 25.5 | 0 | 146 | 0 | 0 | 0 | 1085 | 0 | 51 | 126 | 36 | 0 | 250 | 345 | 12 | 180 | 31 | 90 | 50 | 200 | 38 | 6 | 114 | 44 | 52.2 | 0 | 30 | 270 | 0 | 364 | 36 | 30 | 0 | 162 | 0 | 0 | 78 | 30 | 0 | 17 | 174 | 0 | 96 | 60 | 11 | 0 | 0 | 12 | 7824.7 | 879 | 220 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1072 | 17 | 1439.03 | 0 | 0 | 0 | 40 | 11 | 62 | 0 | 37 | 0 | 0 | 0 | 0 | 205 | 0 | 196 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 164 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 105 | 220 | 0 | 347 | 1110 | 17 | 7114.03 | 14938.73 | 77.99
20:00 | 16 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 17 | 111 | 117 | 80 | 15 | 35 | 90 | 0 | 67 | 300 | 295 | 250 | 0 | 35 | 0 | 273 | 0 | 0 | 0 | 52 | 18 | 21 | 0 | 300 | 0 | 0 | 50 | 0 | 0 | 101 | 76 | 0 | 88 | 36 | 0 | 40 | 0 | 5 | 552 | 0 | 0 | 45 | 25.5 | 0 | 145 | 0 | 0 | 0 | 1147 | 0 | 51 | 60 | 55 | 0 | 245 | 345 | 40 | 191 | 32 | 90 | 70 | 191 | 39 | 6 | 114 | 46 | 52.2 | 0 | 30 | 290 | 0 | 346 | 38 | 30 | 0 | 152 | 0 | 0 | 78 | 30 | 0 | 17 | 173 | 2 | 100 | 128 | 11 | 0 | 0 | 12 | 7931.7 | 879 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 34 | 1447.02 | 0 | 0 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 198 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 162 | 50 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 105 | 220 | 0 | 318 | 1150 | 0 | 6973.02 | 14904.72 | 77.98
21:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 54 | 17 | 112 | 147 | 15 | 0 | 35 | 90 | 0 | 67 | 300 | 290 | 250 | 0 | 35 | 0 | 268 | 0 | 0 | 0 | 52 | 17.5 | 21 | 0 | 300 | 0 | 0 | 16 | 0 | 0 | 100 | 76 | 0 | 100 | 36 | 0 | 40 | 0 | 8 | 557 | 0 | 0 | 20 | 8 | 0 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 73 | 0 | 250 | 345 | 53 | 180 | 33 | 90 | 70 | 170 | 39 | 18 | 114 | 44 | 8 | 0 | 31 | 295 | 0 | 356 | 38 | 30 | 0 | 134 | 0 | 0 | 78 | 30 | 0 | 17 | 173 | 17 | 96 | 165 | 11 | 0 | 0 | 12 | 7872.5 | 926 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 52 | 1449 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 200 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 165 | 51 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 105 | 220 | 0 | 345 | 1244 | 0 | 7172 | 15044.5 | 77.97
22:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 54 | 17 | 113 | 147 | 15 | 0 | 35 | 90 | 0 | 67 | 300 | 260 | 250 | 0 | 35 | 0 | 277 | 0 | 0 | 0 | 52 | 17 | 21 | 0 | 300 | 0 | 0 | 12 | 0 | 0 | 101 | 76 | 0 | 100 | 80 | 0 | 40 | 0 | 17 | 557 | 0 | 0 | 19 | 8 | 0 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 43 | 73 | 0 | 240 | 345 | 51 | 205 | 33 | 90 | 70 | 161 | 38 | 20 | 114 | 46 | 8 | 0 | 31 | 310 | 0 | 400 | 38 | 30 | 0 | 153 | 0 | 0 | 78 | 30 | 0 | 17 | 174 | 17 | 96 | 169 | 8 | 0 | 0 | 12 | 8012 | 926 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 51 | 1440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 197 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 164 | 52 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 115 | 220 | 0 | 415 | 1244 | 0 | 7051 | 15063 | 77.96
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 17 | 113 | 147 | 145 | 0 | 35 | 90 | 0 | 67 | 300 | 260 | 250 | 0 | 35 | 0 | 260 | 0 | 0 | 0 | 125 | 17.5 | 21 | 0 | 300 | 0 | 0 | 12 | 0 | 0 | 101 | 76 | 0 | 100 | 100 | 0 | 40 | 0 | 22 | 557 | 53 | 0 | 19 | 8 | 0 | 147 | 0 | 0 | 0 | 1225 | 0 | 51 | 75 | 73 | 0 | 243 | 345 | 52 | 195 | 33 | 79 | 70 | 159 | 39 | 20 | 114 | 48 | 43 | 0 | 31 | 315 | 0 | 359 | 37 | 30 | 0 | 153 | 0 | 0 | 78 | 30 | 0 | 17 | 174 | 17 | 65 | 170 | 8 | 0 | 0 | 12 | 8254.5 | 926 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 51 | 1451 | 0 | 0 | 0 | 85 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 190 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 168 | 52 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 11 | 115 | 220 | 0 | 343 | 1244 | 35 | 6968 | 15222.5 | 77.95
Total KWH | 226080 | 926400 | 470880 | 0 | 0 | 0 | 0 | 0 | 8521200 | 0 | 0 | 582840 | 403920 | 2626416 | 2218560 | 3212138 | 780632 | 593369 | 1771200 | 0 | 796800 | 7661500 | 6759156 | 6127176 | 0 | 600325 | 0 | 6278166 | 0 | 0 | 214565 | 1497600 | 379200 | 498240 | 0 | 7565454.55 | 489273 | 474218 | 432000 | 0 | 53280 | 1429261 | 991392 | 195504 | 2243520 | 1632000 | 26926 | 946500 | 878182 | 277440 | 12443636.36 | 1134109 | 0 | 689760 | 294458.4 | 749382 | 3450145 | 0 | 0 | 0 | 27654543 | 129195 | 1148676 | 2072509 | 2442182 | 0 | 4412400 | 8090000 | 932160 | 4856000 | 780552 | 1660800 | 1356820 | 3679200 | 441840 | 385560 | 2696100 | 998400 | 957758 | 497845 | 752032 | 7407000 | 0 | 8532000 | 866000 | 677640 | 0 | 3496418 | 80112 | 0 | 1727040 | 674688 | 0 | 389000 | 4574170 | 132840 | 1480800 | 2544000 | 320640 | 13000 | 273250 | 289440 | 188965414.31 | 22062545 | 5615136 | 0 | 30720 | 4096 | 0 | 0 | 0 | 0 | 0 | 0 | 712800 | 22720004 | 410400 | 33168454.06 | 0 | 162669 | 0 | 1442592 | 83793 | 352480 | 743712 | 136390 | 176746 | 783450 | 0 | 355496 | 4792364 | 0 | 4710745 | 0 | 0 | 0 | 8651345 | 0 | 29040 | 0 | 4072000 | 1164218 | 1623495 | 227110 | 1913664 | 0 | 0 | 47560.8 | 1355760 | 5013 | 471360 | 6501000 | 237063 | 2605000 | 5216510 | 0 | 8660952 | 27015272.73 | 529200 | 168790155.59 | 357755569.9

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14736.73 | MW | 12:00 Hr. | Energy Generated |  |  | 357.7556 |  | MKWHr.
| Day Peak Demand |  |  | 14952.73 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.799 |  | MKWHr.
| Evening Peak Generation |  |  | 15044.5 | MW | 21:00 Hr. | Energy Demand |  |  | 362.5546 |  | MKWHr.
| Evening Peak Demand |  |  | 15044.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 38 |  | °C
| Minimum Generation of the Day |  |  | 13596.17 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 988.58 |  | MMCFD
| Maximum Generation of the Day |  |  | 16364.16 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.2484 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.7901 | 0 | 16.7072 | 0 | 0 | 0.21457 | 0 | 0 | 60.7118 | Gas | 132.4949 | Gas | 473114239.3635
| Chattogram Zone |  |  | 3.7276 | 40.0982 | 11.6331 | 0 | 0.9465 | 0.15612 | 0 | 0.05328 | 56.6147 | Coal | 110.2316 | Coal | 730829057.7165
| Cumilla Zone |  |  | 24.4044 | 0 | 12.2602 | 0 | 0 | 0.49784 | 0.9984 | 0 | 38.1608 | HFO | 53.1289 | HFO | 999317760.438
| Mymensingh Zone |  |  | 0.32064 | 0 | 4.4471 | 0 | 0 | 0.28625 | 0 | 0 | 5.054 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.4241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4241 | Hydro | 0.9465 | Hydro | 94650
| Khulna Zone |  |  | 5.6151 | 22.72 | 0.44522 | 0 | 0 | 0.7128 | 22.0625 | 0 | 51.5557 | Solar | 4.671 | Solar | 75861439.898
| Barishal Zone |  |  | 8.0586 | 42.1772 | 1.0006 | 0 | 0 | 0.005013 | 0 | 0 | 51.2414 | Import | 56.2294 | Import | 313152032.6504
| Rajshahi Zone |  |  | 18.1545 | 0 | 3.0984 | 0 | 0 | 1.168 | 33.1685 | 0 | 55.5893 | Wind | 0.05328 | Wind | 780019.2
| Rangpur Zone |  |  | 0 | 5.2362 | 3.5372 | 0 | 0 | 1.6304 | 0 | 0 | 10.4038
| Total |  |  | 132.4949 | 110.2316 | 53.1289 | 0 | 0.9465 | 4.671 | 56.2294 | 0.05328 | 357.7556
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 473114239.3635 |  | Hydro | 94650
|  |  |  | Coal | 730829057.7165 |  | Solar | 75861439.898
|  |  |  | HFO | 999317760.438 |  | Import | 313152032.6504
|  |  |  | HSD | 0 |  | Wind | 780019.2
[5 empty] | Total: | 259,31,49,199 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0625 | Peak Hr Flow | 926.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44559400.08 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.1685 | Peak Hr Flow | 1449.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 798 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9984 | Peak Hr Flow | 44.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 916 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.2294 | Peak Hr Flow | 2419.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5341
|  |  |  | Chattogram |  | 0 |  | 1542
|  |  |  | Cumilla |  | 0 |  | 1385
|  |  |  | Mymensingh |  | 0 |  | 1075
|  |  |  | Sylhet |  | 0 |  | 443
|  |  |  | Khulna |  | 0 |  | 1982
|  |  |  | Barishal |  | 0 |  | 522
|  |  |  | Rajshahi |  | 0 |  | 1617
|  |  |  | Rangpur |  | 0 |  | 709
|  |  |  | Total |  | 0 |  | 14616
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Meghnaghat CCPP(Summit) GT-1 |  |  | 110 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 410 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 845.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 10:36 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to 33 kv pirojpur pbs | [7 empty] | 30.0MW load
|  |  | feeder red hot maintenance work. | [7 empty] | interrup.
|  | 08:30 | Kodda 132/33kV S/S Tr-2 (416T) HT is restored.
|  | 08:30 | Munshiganj 132/33kV S/S Transformer-2 LT is restored.
|  | 08:31 | Kodda 132/33kV S/S Tr-2 (416T) LT is restored.
| 08:42 | 10:54 | Sylhet 132/33kV S/S T1 HT Forced S/D Due to Red hot Maintenance of Upashahar feeder. | [7 empty] | 28.0MW load
interrup.
| 08:42 | 10:54 | Sylhet 132/33kV S/S T1 LT Forced S/D Due to Red hot Maintenance of Upashahar feeder. | [7 empty] | 28.0MW load
interrup.
| 09:04 | 11:50 | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to 132kV CB(R-phase) clamp
connector maintenance due to high temperature.
| 09:05 | 11:44 | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to 132kV CB(R-phase) clamp
connector maintenance due to high temperature.
|  | 09:16 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT is restored.
|  | 09:16 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT is restored.
| 09:21 | 12:20 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D
| 09:21 | 12:21 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D
|  | 09:27 | Kushtia 132/33kV S/S T2 HT is restored.
|  | 09:27 | Kushtia 132/33kV S/S T2 LT is restored.
|  | 10:03 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 is restored.
| 10:06 | 12:13 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Red Hot Maintenance by PBS | [7 empty] | 28.0MW load
interrup.
| 10:07 | 12:12 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Red Hot Maintenance by PBS | [7 empty] | 28.0MW load
interrup.
| 10:12 | 17:30 | Kachua 132/33kV S/S Main Bus-2 Project Work S/D Due to ESPNER project work
|  | 10:17 | Ghorashal 230kV S/S TARFO-2 HT is restored.
|  | 10:29 | Ghorashal 230kV S/S TARFO-2 LT is restored.
| 11:13 | 12:33 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Inst. E/F, | [7 empty] | 43.0MW load
|  |  | Dist. Relay. relays Due to Unknown. | [7 empty] | interrup. Barishal
132/33kV end
| 11:45 | 12:16 | Kabirpur 132/33kV S/S XFR, T-I LT Tripped showing Micomp127 relays Due to Trip | [7 empty] | 200.0MW load
interrup.
| 11:45 | 00:21 | Kabirpur 132/33kV S/S XFR, T-2 HT Tripped showing Trip ckt supervissin relay relays Due | [7 empty] | 130.0MW load
|  |  | to MK box wiring brunt | [7 empty] | interrup.
| 11:45 | 12:16 | Kabirpur 132/33kV S/S XFR, T-I LT Tripped showing Micomp127 relays Due to Trip | [7 empty] | 200.0MW load
interrup.
| 11:45 | 00:22 | Kabirpur 132/33kV S/S XFR, T-2 LT Tripped showing Micom p127 relays Due to Trip | [7 empty] | 130.0MW load
interrup.
| 12:00 |  | day peak genration 14733MW
| 15:30 | 18:50 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing O/C,Earth Fault Relay relays Due to 33
KV Bus loop and BISIC Feeder Earth Fault
| 15:30 | 18:50 | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing O/C,Earth Fault Relay relays Due to
33KV BUs Loop and BISIC Feeder Earth Fault
| 16:21 | 16:33 | Jamalpur-Mymensingh 132kV Ckt-2 Tripped from Jamalpur 132/33kV end showing A,N relays.
| 17:00 | 17:07 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Distance Relay
relays.
| 17:02 | 17:11 | Cumilla(S) 132/33kV S/S TR-4 LT Tripped showing 1.RET650 2.REF615 relays Due to 33 KV | [7 empty] | 26.0MW load
|  |  | Shafiul Alam Feeder fault(PDB) | [7 empty] | interrup.
| 17:10 |  | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Tripped showing Distance Relay relays.
|  | 17:20 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
| 17:30 | 17:42 | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Hasnabad 132/33kV end showing Master Trip
Relay relays.
| 18:44 | 18:55 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Micom-P142 relays Due to Due to
33kv Sukanpukur Feeder fault.
| 21:00 |  | Evening Peak Generation: 15044 MW.
| 21:44 |  | Rampal 1320 MW (BIFPCL) unit-1 tripped.
| 21:44 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1 tripped-21:44
| 21:44 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
| 22:06 | 22:43 | Mithapukur-Palashbari 132kV Ckt-2 Tripped from Palashbari 132/33kV end showing Distance
relay relays. and from Mithapukur 132/33kV end showing 21M1, 22M2, 86A, 86B relays.
| 22:21 | 23:14 | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Bhandaria 132/33kV end Due to Red hot | [7 empty] | 30.0MW load
|  |  | maintenance of barishal grid end. and from Barishal 132/33kV end Due to For R phase line | [7 empty] | interrup. Bhandaria
|  |  | side temperature rise mitigate works. | [7 empty] | 132/33kV end and
25.0MW load
interrup. Barishal
132/33kV end
| 23:39 |  | Meghnaghat Summit CCPP 335 MW GT-1 was shutdown due to scheduled maintenance.
| 23:41 |  | Meghnaghat CCPP(Summit) GT-1 Planned Shutdown with remarks:- GT-1 Shutdown for
maintenance at 23:41 hrs
| 03:23 |  | Summit Meghnaghat-2 589 MW CCPP tripped due to a problem in Fuel Gas Compressor.
| 03:23 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- GT
| 04:02 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 05:23 |  | Summit Meghnaghat-2 589 MW CCPP GT was sync.
| 05:23 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 06:04 | 07:43 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end Due to S/D
taken by NLDC and from Narshingdi 132/33kV end Due to Hotspot maintenance work
| 06:07 | 07:35 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to
Hotspot maintenance work
| 06:10 | 07:35 | Narshingdi 132/33kV S/S 132 kV Main Bus-2 Scheduled S/D Due to Hotspot maintenance work
| 07:28 |  | Jhenaidah 132/33kV S/S Jhenaidah1-Jhenaidah2,132kV Circuit-2(L3) Forced S/D Due to
Maintenance work for jhenaidah 230 kv ss.
| 07:28 |  | Jhenaidah 230/132kV S/S Jhenaidah (New)-Jhenaidah (Old) Ckt-2 Scheduled S/D Due to Faulty
energy meter replacement work
| 07:50 |  | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing O/C, E/F Relay relays Due to
Chunarughat feeder O/C Earth fault Relay.
| 07:50 |  | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing O/C , E/F Relay relays Due to
Chunarughat feeder O/C Earth fault Relay.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 341 | 8521200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7661500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 6759156 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 780632 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 268 | 6278166 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 226080 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 582840 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 2218560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 593369 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 600325 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17.5 | 379200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 498240 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 470880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 3212138 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 2626416 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 926400 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 796800 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1771200 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 214565 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 403920 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 7565454.55 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 250 | 6127176 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 52 | 1497600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2488.5 | 60711817.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 294458.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 129195 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 689760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 946500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 148 | 3450145 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 749382 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 76 | 991392 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 100 | 1429261 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2243520 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 277440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 16 | 432000 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26926 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 474218 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 195504 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 878182 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 1632000 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 489273 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 1134109 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27654543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 53280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 557 | 12443636.36 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2333 | 56614724.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 180 | 4856000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 250 | 4412400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8090000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 780552 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 53 | 932160 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 73 | 2442182 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1148676 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 30 | 2072509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 31 | 752032 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1356820 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3679200 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 44 | 998400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 957758 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 385560 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2696100 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 39 | 441840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1660800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 497845 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1599 | 38160834
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 320640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 165 | 2544000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1480800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 273250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 289440 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 132840 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 301 | 5053970
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 866000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 677640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 134 | 3496418 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 674688 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1727040 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 4574170 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 389000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 80112 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7407000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 356 | 8532000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under maintenance
Sylhet Area Total |  |  |  |  | 2368.568 | 1151 | 28424068
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 926 | 22062545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 30720 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 4096 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 212 | 5615136 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 410400 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 712800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1220 | 22720004 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2410 | 51555701
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 345 | 8660952 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 471360 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 237063 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 105 | 2605000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27015272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5216510 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 529200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6501000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5013 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2248 | 51241370.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 162669 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 3 | 83793 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 136390 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 206 | 4792364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4710745 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 370 | 8651345 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 176746 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 352480 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 1442592 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 743712 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29040 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1449 | 33168454.06 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 355496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 783450 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2228 | 55589276.06
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1164218 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 4072000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 1913664 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47560.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 1623495 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 227110 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1355760 | -
Rangpur Area Total |  |  |  |  | 950 | 286 | 10403807.8
Eastern Grid Total |  |  |  |  | 16921.242 | 7872.5 | 188965414.31
Western Grid Total |  |  |  |  | 11702.84 | 7172 | 168790155.59
National Grid Total |  |  |  |  | 28624.082 | 15044.5 | 357755569.9
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9785.78 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4830.1 | MW
i) Dhaka area |  |  | 5340.69 |  | MW | i) Khulna area |  |  |  | 1981.8 | MW
ii) Chattogram area |  |  | 1542 |  | MW | ii) Barishal area |  |  |  | 522.1 | MW
iii) Cumilla area |  |  | 1385.09 |  | MW | iii) Rajshahi area |  |  |  | 1617.2 | MW
iv) Mymensingh area |  |  | 1075 |  | MW | iv) Rangpur area |  |  |  | 709 | MW
v) Sylhet area |  |  | 443 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14615.88 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 91 | 19:30 | 133 | Patuakhali | 80 | 01:00
2 | AKSML | 106 | 07:00 | 68 | Jaldhaka | 66 | 14:00 | 134 | Payra | 38 | 00:00
3 | Aftabnagar | 46 | 00:00 | 69 | Jamalpur | 129 | 16:00 | 135 | Postogola | 67 | 16:00
4 | Agargaon | 147 | 00:00 | 70 | Jashore | 149 | 00:00 | 136 | Purbachal | 24 | 00:00
5 | Agrabad | 106 | 19:00 | 71 | Jhenaidah | 154 | 19:30 | 137 | Purbasadipur | 142 | 14:00
6 | Amnura | 48 | 13:00 | 72 | Joydebpur | 160 | 19:00 | 138 | Rahanpur | 32 | 19:00
7 | Ashuganj | 94 | 03:00 | 73 | Joypurhat | 80 | 02:00 | 139 | Rahim | 57 | 14:00
8 | BSRM | 197 | 20:00 | 74 | Juldah | 18 | 01:00 | 140 | Rajbari | 95 | 19:30
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 27 | 20:00 | 141 | Rajendrapur | 146 | 15:00
10 | Bajitpur | 55 | 00:00 | 76 | Kabirpur | 287 | 09:00 | 142 | Rajshahi | 142 | 00:00
11 | Bakulia | 110 | 16:00 | 77 | Kachua | 96 | 03:00 | 143 | Rajshahi-230 | 103 | 13:00
12 | Banani | 41 | 16:00 | 78 | Kallyanpur | 123 | 17:00 | 144 | Ramganj | 116 | 17:00
13 | Bangabhaban | 6 | 11:00 | 79 | Kalurghat | 42 | 16:00 | 145 | Rampur | 51 | 00:00
14 | Barapukuria | 76 | 19:30 | 80 | Kamrangirchar | 70 | 15:00 | 146 | Rangamati | 16 | 00:00
15 | Barguna | 34 | 23:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 155 | 14:00
16 | Barishal | 111 | 00:00 | 82 | Kasba | 38 | 00:00 | 148 | Ruppur | 8 | 11:00
17 | Barishal-230 | 126 | 23:00 | 83 | Kazla | 110 | 16:00 | 149 | SSM | 8 | 00:00
18 | Baroaulia | 72 | 00:00 | 84 | Keranigonj | 93 | 17:00 | 150 | Saidpur | 122 | 14:00
19 | Baroirhat | 79 | 00:00 | 85 | Khagrachori | 32 | 00:00 | 151 | Satkhira | 147 | 19:00
20 | Bashundhara | 226 | 16:00 | 86 | Khulna | 79 | 00:00 | 152 | Satmasjid | 128 | 16:00
21 | BashundharaCement | 12 | 07:00 | 87 | Khulshi | 202 | 00:00 | 153 | Savar | 238 | 19:00
22 | Beanibazar | 74 | 00:00 | 88 | Kishoreganj | 144 | 00:00 | 154 | SevenRings | 18 | 13:00
23 | Benapole | 76 | 19:30 | 89 | Kodda | 304 | 23:00 | 155 | ShahCement | 36 | 10:00
24 | Bhaluka | 167 | 00:00 | 90 | Kulaura | 56 | 00:00 | 156 | Shahjadpur | 96 | 08:00
25 | Bhandaria | 59 | 00:00 | 91 | Kurigram | 56 | 02:00 | 157 | Shahjibazar | 118 | 01:00
26 | Bhangura | 52 | 19:00 | 92 | Kushtia | 176 | 19:00 | 158 | Shahmirpur | 67 | 00:00
27 | Bheramara(GK) | 74 | 00:00 | 93 | Lalbag | 70 | 11:00 | 159 | Shariatpur | 94 | 00:00
28 | Bhulta | 239 | 05:00 | 94 | Lalmonirhat | 50 | 01:00 | 160 | Sherpur | 134 | 13:00
29 | Bog-Sherpur | 76 | 03:00 | 95 | MI_Cement | 18 | 12:00 | 161 | Shikalbaha | 33 | 01:00
30 | Bogura | 193 | 05:00 | 96 | Madanganj | 56 | 00:00 | 162 | Shitalakhya | 97 | 17:00
31 | Borhanuddin | 102 | 23:00 | 97 | Madaripur | 132 | 00:00 | 163 | Sholosohor | 52 | 19:30
32 | Brahmanbaria | 125 | 00:00 | 98 | Madartek | 113 | 01:00 | 164 | Shyampur | 200 | 11:00
33 | Cantonment | 168 | 16:00 | 99 | Madunaghat | 66 | 19:00 | 165 | Siddhirganj | 136 | 15:00
34 | Chandina | 24 | 19:00 | 100 | Magura | 74 | 20:00 | 166 | Sirajganj | 126 | 00:00
35 | Chandpur | 78 | 20:00 | 101 | Mahasthangarh | 92 | 02:00 | 167 | Sonargaon | 118 | 20:00
36 | Chandraghona | 40 | 19:00 | 102 | Manikganj | 144 | 19:30 | 168 | Sreemongol | 87 | 00:00
37 | Chapai | 72 | 14:00 | 103 | Maniknagar | 72 | 00:00 | 169 | Sreepur | 107 | 12:00
38 | Charsaidpur | 48 | 01:00 | 104 | Matarbari | 54 | 00:00 | 170 | Srinagar | 50 | 02:00
39 | Chauddagram | 77 | 03:00 | 105 | Matuail | 72 | 15:00 | 171 | Sunamganj | 63 | 02:00
40 | Chhatak | 37 | 00:00 | 106 | Millgate | 134 | 15:00 | 172 | Sylhet | 51 | 00:00
41 | Chowmuhani | 230 | 18:00 | 107 | Mirpur | 153 | 14:00 | 173 | Sylhet-132 | 122 | 00:00
42 | Chuadanga | 129 | 00:00 | 108 | Mirsorai | 11 | 15:00 | 174 | TK | 26 | 18:30
43 | Coxsbazar | 145 | 18:30 | 109 | Mirzapur | 52 | 20:00 | 175 | Tangail | 210 | 20:00
44 | Cumilla(N) | 158 | 15:00 | 110 | Mithapukur | 74 | 19:00 | 176 | Thakurgaon | 105 | 19:30
45 | Cumilla(S) | 197 | 15:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 124 | 12:00
46 | Daudkandi | 152 | 21:00 | 112 | Mogbazar | 163 | 17:00 | 178 | Ullahpara | 48 | 01:00
47 | Dhaka | 52 | 13:00 | 113 | Mongla | 42 | 15:00 | 179 | Ullon | 65 | 00:00
48 | Dhamrai | 142 | 06:00 | 114 | Motijheel | 44 | 16:00 | 180 | Uttara | 111 | 16:00
49 | Dhanmondi | 160 | 16:00 | 115 | Muktagacha | 39 | 06:00 | 181 | UttaraNew | 60 | 00:00
50 | Dohazari | 111 | 19:30 | 116 | Munshiganj | 113 | 02:00 | 182 | Zigatola | 83 | 12:00
51 | Faridpur | 179 | 00:00 | 117 | Muradnagar | 27 | 00:00
52 | Fatullah | 111 | 15:00 | 118 | Mymensingh | 203 | 01:00
53 | Fenchuganj | 44 | 00:00 | 119 | Naogaon | 155 | 01:00
54 | Feni | 131 | 19:00 | 120 | Narail | 67 | 20:00
55 | GPH | 93 | 20:00 | 121 | Narinda | 81 | 13:00
56 | Ghatail | 78 | 19:30 | 122 | Narshingdi | 181 | 21:00
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 179 | 00:00
58 | Ghorashal-230 | 98 | 21:00 | 124 | Nawabganj | 66 | 20:00
59 | Goalpara | 46 | 22:00 | 125 | Netrakona | 123 | 10:00
60 | Gollamari | 104 | 00:00 | 126 | New | 92 | 12:00
61 | Gopalganj | 122 | 19:30 | 127 | Niamatpur | 91 | 00:00
62 | Gulshan | 124 | 15:00 | 128 | Noapara | 64 | 21:00
63 | Halishahar | 88 | 15:00 | 129 | PHP | 8 | 13:00
64 | HaripurSBU | 185 | 11:00 | 130 | Pabna | 135 | 00:00
65 | Hasnabad | 91 | 17:00 | 131 | Palashbari | 140 | 00:00
66 | Hathazari | 91 | 00:00 | 132 | Panchagarh | 51 | 01:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 16364.16 | 312 |  | 16690.2
1:00 | 16092.96 | 437 |  | 16549.96
2:00 | 15847.37 | 434 |  | 16300.9
3:00 | 15492.92 | 343 |  | 15851.36
4:00 | 15104.12 | 331 |  | 15450.02
5:00 | 14886.46 | 301 |  | 15201.01
6:00 | 13995.53 | 293 |  | 14301.72
7:00 | 13739.33 | 252 |  | 14002.67
8:00 | 13596.17 | 245 |  | 13852.17
9:00 | 13814.89 | 181 |  | 14003.89
10:00 | 13959.55 | 158 |  | 14124.55
11:00 | 14381.97 | 182 |  | 14571.97
12:00 | 14736.73 | 207 |  | 14952.73
13:00 | 15158.72 | 217 |  | 15385.72
14:00 | 15555.55 | 256 |  | 15823.55
15:00 | 15442.93 | 248 |  | 15701.93
16:00 | 14856.12 | 170 |  | 15033.77
17:00 | 13946.11 | 35 |  | 13982.69
18:00 | 12767.83 | 0 |  | 12767.83
19:00 | 13940.94 | 48 |  | 13990.94
19:30 | 14938.73 | 50 |  | 14990.73
20:00 | 14904.72 | 39 |  | 14945.72
21:00 | 15044.5 | 0 |  | 15044.5
22:00 | 15063 | 64 |  | 15130
23:00 | 15222.5 | 46 |  | 15270.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8779.2 | 7584.96 | 16364.16 | DAILY GENERATION CURVE
00:30 | 8692.95 | 7535.61 | 16228.56
01:00 | 8606.7 | 7486.26 | 16092.96 | 11-05-2025
01:30 | 8495.45 | 7474.715 | 15970.165
02:00 | 8384.2 | 7463.17 | 15847.37
02:30 | 8394.2 | 7275.945 | 15670.145
03:00 | 8404.2 | 7088.72 | 15492.92
03:30 | 8291.45 | 7007.07 | 15298.52
04:00 | 8178.7 | 6925.42 | 15104.12
04:30 | 8096.2 | 6899.09 | 14995.29
05:00 | 8013.7 | 6872.76 | 14886.46
05:30 | 7699.16 | 6741.835 | 14440.995
06:00 | 7384.62 | 6610.91 | 13995.53
06:30 | 7178.22 | 6689.21 | 13867.43
07:00 | 6971.82 | 6767.51 | 13739.33
07:30 | 6846.715 | 6821.035 | 13667.75
08:00 | 6721.61 | 6874.56 | 13596.17
08:30 | 6803.315 | 6902.215 | 13705.53
09:00 | 6885.02 | 6929.87 | 13814.89
09:30 | 7004.87 | 6882.35 | 13887.22
10:00 | 7124.72 | 6834.83 | 13959.55
10:30 | 7261.645 | 6909.115 | 14170.76
11:00 | 7398.57 | 6983.4 | 14381.97
11:30 | 7544.385 | 7014.965 | 14559.35
12:00 | 7690.2 | 7046.53 | 14736.73
12:30 | 7835.855 | 7111.87 | 14947.725
13:00 | 7981.51 | 7177.21 | 15158.72
13:30 | 8048.84 | 7308.295 | 15357.135
14:00 | 8116.17 | 7439.38 | 15555.55
14:30 | 8127.805 | 7371.435 | 15499.24
15:00 | 8139.44 | 7303.49 | 15442.93
15:30 | 8057.02 | 7092.505 | 15149.525
16:00 | 7974.6 | 6881.52 | 14856.12
16:30 | 7805.21 | 6595.905 | 14401.115
17:00 | 7635.82 | 6310.29 | 13946.11
17:30 | 7146.365 | 6210.605 | 13356.97
18:00 | 6656.91 | 6110.92 | 12767.83
18:30 | 7051.405 | 6302.98 | 13354.385
19:00 | 7445.9 | 6495.04 | 13940.94
19:30 | 7824.7 | 7114.03 | 14938.73
20:00 | 7931.7 | 6973.02 | 14904.72
20:30 | 7902.1 | 7072.51 | 14974.61 |  | Executive Engineer
21:00 | 7872.5 | 7172 | 15044.5 |  | Network Operation Division
21:30 | 7942.25 | 7111.5 | 15053.75
22:00 | 8012 | 7051 | 15063
22:30 | 8133.25 | 7009.5 | 15142.75
23:00 | 8254.5 | 6968 | 15222.5

## En-Curve
QF-LDC-12
Date | 11-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3250 | 2286 | 780 | 0 | 52 | 1363.96 | 40 | 5024 | 0 | 808 | 2760.2 | 0 | 0 | 0 | 312 | DAILY ENERGY CURVE
00:30 | 3173.5 | 2301 | 850.5 | 0 | 52 | 1358.61 | 40 | 5014.5 | 0 | 738.5 | 2699.95 | 0 | 0 | 0 | 374.5 | 11-05-2025
01:00 | 3097 | 2316 | 921 | 0 | 52 | 1353.26 | 40 | 5005 | 0 | 669 | 2639.7 | 0 | 0 | 0 | 437
01:30 | 3140 | 2313.25 | 922 | 0 | 51 | 1357.715 | 40 | 4979 | 0 | 554 | 2613.2 | 0 | 0 | 0 | 435.5 | Energy Generated | 357.7556 |  | MKWHr
02:00 | 3183 | 2310.5 | 923 | 0 | 50 | 1362.17 | 40 | 4953 | 0 | 439 | 2586.7 | 0 | 0 | 0 | 434 | Energy not Served | 4.799 |  | MKWHr
02:30 | 3142 | 2315.5 | 923 | 0 | 49 | 1360.445 | 40 | 4771 | 0 | 428 | 2641.2 | 0 | 0 | 0 | 388.5 | Total Energy Requirement | 362.5546 |  | MKWHr
03:00 | 3101 | 2320.5 | 923 | 0 | 48 | 1358.72 | 40 | 4589 | 0 | 417 | 2695.7 | 0 | 0 | 0 | 343
03:30 | 3096.5 | 2323 | 922.5 | 0 | 48 | 1359.07 | 40 | 4587 | 0 | 377 | 2545.45 | 0 | 0 | 0 | 337
04:00 | 3092 | 2325.5 | 922 | 0 | 48 | 1359.42 | 40 | 4585 | 0 | 337 | 2395.2 | 0 | 0 | 0 | 331
04:30 | 3199.5 | 2311 | 922 | 0 | 46 | 1361.09 | 40 | 4584.5 | 0 | 344.5 | 2186.7 | 0 | 0 | 0 | 316
05:00 | 3307 | 2296.5 | 922 | 0 | 44 | 1362.76 | 40 | 4584 | 0 | 352 | 1978.2 | 0 | 0 | 0 | 301
05:30 | 3271 | 2237.25 | 922 | 0 | 43 | 1370.92 | 40 | 4598 | 15.225 | 294.5 | 1649.1 | 0 | 0 | 0 | 297
06:00 | 3235 | 2178 | 922 | 0 | 42 | 1379.08 | 40 | 4612 | 30.45 | 237 | 1320 | 0 | 0 | 0 | 293
06:30 | 3246 | 2219 | 922 | 0 | 41 | 1381.675 | 40 | 4629.5 | 86.755 | 225.5 | 1076 | 0 | 0 | 0 | 272.5
07:00 | 3257 | 2260 | 922 | 0 | 40 | 1384.27 | 40 | 4647 | 143.06 | 214 | 832 | 0 | 0 | 0 | 252
07:30 | 3322 | 2164 | 899 | 0 | 39 | 1354.965 | 40 | 4612.5 | 218.285 | 214 | 804 | 0 | 0 | 0 | 248.5
08:00 | 3387 | 2068 | 876 | 0 | 38 | 1325.66 | 40 | 4578 | 293.51 | 214 | 776 | 0 | 0 | 0 | 245
08:30 | 3390 | 2070.5 | 876 | 0 | 33 | 1321.135 | 40 | 4555 | 367.295 | 222 | 830.6 | 0 | 0 | 0 | 213
09:00 | 3393 | 2073 | 876 | 0 | 28 | 1316.61 | 40 | 4532 | 441.08 | 230 | 885.2 | 0 | 0 | 0 | 181
09:30 | 3379.5 | 2071 | 899.5 | 0 | 31 | 1285.26 | 40 | 4465.5 | 494.26 | 229 | 992.2 | 0 | 0 | 0 | 169.5
10:00 | 3366 | 2069 | 923 | 0 | 34 | 1253.91 | 40 | 4399 | 547.44 | 228 | 1099.2 | 0 | 0 | 0 | 158
10:30 | 3369.5 | 2096 | 923 | 0 | 33 | 1260.23 | 40 | 4443 | 574.33 | 226.5 | 1205.2 | 0 | 0 | 0 | 170
11:00 | 3373 | 2123 | 923 | 0 | 32 | 1266.55 | 40 | 4487 | 601.22 | 225 | 1311.2 | 0 | 0 | 0 | 182
11:30 | 3335.5 | 2119 | 922.5 | 0 | 35 | 1314.56 | 40 | 4518.5 | 623.09 | 239.5 | 1411.2 | 0 | 0 | 0.5 | 194.5
12:00 | 3298 | 2115 | 922 | 0 | 38 | 1362.57 | 40 | 4550 | 644.96 | 254 | 1511.2 | 0 | 0 | 1 | 207
12:30 | 3310 | 2132.75 | 922 | 0 | 43 | 1360.185 | 40 | 4568.5 | 630.09 | 287.5 | 1648.7 | 0 | 0 | 5 | 212
13:00 | 3322 | 2150.5 | 922 | 0 | 48 | 1357.8 | 40 | 4587 | 615.22 | 321 | 1786.2 | 0 | 0 | 9 | 217
13:30 | 3299.5 | 2147.25 | 923 | 0 | 46 | 1359.985 | 40 | 4623 | 578.3 | 324 | 2006.6 | 0 | 0 | 9.5 | 236.5
14:00 | 3277 | 2144 | 924 | 0 | 44 | 1362.17 | 40 | 4659 | 541.38 | 327 | 2227 | 0 | 0 | 10 | 256
14:30 | 3266 | 2166 | 923.5 | 0 | 47 | 1364.37 | 38.5 | 4632.5 | 463.27 | 327.5 | 2257.1 | 0 | 0 | 13.5 | 252
15:00 | 3255 | 2188 | 923 | 0 | 50 | 1366.57 | 37 | 4606 | 385.16 | 328 | 2287.2 | 0 | 0 | 17 | 248
15:30 | 3231 | 2185.5 | 922.5 | 0 | 49 | 1376.985 | 38 | 4480.5 | 323.09 | 333 | 2196.95 | 0 | 0 | 13 | 209
16:00 | 3207 | 2183 | 922 | 0 | 48 | 1387.4 | 39 | 4355 | 261.02 | 338 | 2106.7 | 0 | 0 | 9 | 170
16:30 | 3120.5 | 2112.5 | 922 | 0 | 45 | 1411.495 | 39.5 | 4216 | 183.92 | 370 | 1973.7 | 0 | 0 | 6.5 | 102.5
17:00 | 3034 | 2042 | 922 | 0 | 42 | 1435.59 | 40 | 4077 | 106.82 | 402 | 1840.7 | 0 | 0 | 4 | 35
17:30 | 2973.5 | 1916 | 921.5 | 0 | 35 | 1440.505 | 40 | 3912 | 62.865 | 415.5 | 1637.6 | 0 | 0 | 2.5 | 17.5
18:00 | 2913 | 1790 | 921 | 0 | 28 | 1445.42 | 40 | 3747 | 18.91 | 429 | 1434.5 | 0 | 0 | 1 | 0
18:30 | 3084.5 | 1907.2 | 900 | 0 | 34 | 1450.23 | 40 | 3956 | 9.455 | 449 | 1523.5 | 0 | 0 | 0.5 | 24
19:00 | 3256 | 2024.4 | 879 | 0 | 40 | 1455.04 | 40 | 4165 | 0 | 469 | 1612.5 | 0 | 0 | 0 | 48
19:30 | 3355 | 1995 | 879 | 0 | 44 | 1439.03 | 40 | 4688 | 0 | 542 | 1956.7 | 0 | 0 | 0 | 50
20:00 | 3335 | 2091 | 879 | 0 | 46 | 1447.02 | 40 | 4809 | 0 | 457 | 1800.7 | 0 | 0 | 0 | 39
20:30 | 3359 | 2105.25 | 902.5 | 0 | 45 | 1448.01 | 40 | 4961 | 0 | 471.5 | 1642.35 | 0 | 0 | 0 | 19.5
21:00 | 3383 | 2119.5 | 926 | 0 | 44 | 1449 | 40 | 5113 | 0 | 486 | 1484 | 0 | 0 | 0 | 0
21:30 | 3444 | 2125.25 | 926 | 0 | 45 | 1444.5 | 40 | 5032 | 0 | 485 | 1512 | 0 | 0 | 0 | 32
22:00 | 3505 | 2131 | 926 | 0 | 46 | 1440 | 40 | 4951 | 0 | 484 | 1540 | 0 | 0 | 0 | 64
22:30 | 3456.5 | 2137.25 | 926 | 0 | 47 | 1445.5 | 40 | 4722 | 0 | 516 | 1852.5 | 0 | 0 | 0 | 55
23:00 | 3408 | 2143.5 | 926 | 0 | 48 | 1451 | 40 | 4493 | 0 | 548 | 2165 | 0 | 0 | 0 | 46
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 18:00 | 369 | 00:00 | Payra | 411 | 18:00 | 403 | 20:00
Ashuganj | 395 | 5:00 | 360 | 23:00 | Rahanpur | 398 | 15:00 | 388 | 21:00
Bhulta | 388 | 05:00 | 364 | 00:00 | Rampal | 393 | 18:00 | 376 | 03:00
Bibiana | 393 | 18:00 | 383 | 00:00
BIPTC | 400 | 09:00 | 389 | 21:00
Bogura | 382 | 01:00 | 370 | 21:00
Gopalganj | 391 | 18:00 | 377 | 00:00
Kaliakoir | 373 | 18:00 | 362 | 00:00
Madunaghat | 395 | 19:00 | 386 | 09:00
Meghnaghat | 387 | 18:00 | 375 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 18:00 | 213 | 11:00 | Keranigonj | 220 | 18:00 | 210 | 13:00
AKSML | 235 | 04:00 | 222 | 12:00 | Khulna(S) | 223 | 18:00 | 210 | 00:00
Aminbazar | 222 | 18:00 | 213 | 14:00 | Madunaghat | 235 | 01:00 | 226 | 08:00
Ashuganj | 229 | 16:00 | 220 | 00:00 | Madunaghat-400 | 236 | 03:00 | 227 | 08:00
Ashuganj-400 | 220 | 5:00 | 210 | 23:00 | Maniknagar | 219 | 18:00 | 210 | 11:00
Baghabari | 232 | 06:00 | 223 | 21:00 | Meghnaghat | 227 | 18:30 | 215 | 00:00
Barapukuria | 226 | 23:00 | 217 | 12:00 | Meghnaghat-400 | 223 | 18:00 | 215 | 11:00
Barapukuria-230 | 225 | 23:00 | 216 | 12:00 | Mirsorai | 235 | 03:00 | 218 | 11:00
Barishal | 234 | 18:00 | 225 | 00:00 | Rajshahi | 232 | 09:00 | 221 | 21:00
Bheramara | 233 | 09:00 | 223 | 21:00 | Rampal | 224 | 18:00 | 211 | 21:00
Bhulta | 225 | 05:00 | 212 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 17:00 | 217 | 00:00 | Rampura | 223 | 05:00 | 210 | 13:00
BIPTC | 235 | 09:00 | 222 | 21:00 | Shikalbaha | 244 | 08:00 | 224 | 08:00
Bogura | 232 | 14:00 | 224 | 21:00 | Shyampur | 221 | 18:00 | 211 | 13:00
Bogura-400 | 232 | 01:00 | 223 | 11:00 | Siddhirganj | 222 | 18:00 | 213 | 11:00
Borhanuddin | 239 | 11:00 | 233 | 00:00 | Sirajgonj | 237 | 04:00 | 232 | 21:00
BSRM | 231 | 02:00 | 218 | 09:00 | Sreepur | 228 | 17:00 | 218 | 13:00
Cumilla(N) | 223 | 18:00 | 213 | 13:00 | Tongi | 221 | 04:00 | 213 | 10:00
Faridpur | 228 | 18:00 | 218 | 00:00
Fenchuganj | 227 | 07:00 | 218 | 00:00
Ghorashal | 230 | 00:00 | 220 | 08:00
Ghorashal-230 | 223 | 05:00 | 213 | 00:00
Gopalganj | 230 | 18:00 | 222 | 00:00
GPH | 233 | 02:00 | 221 | 11:00
Haripur | 221 | 18:00 | 212 | 11:00
Hasnabad | 221 | 18:00 | 212 | 12:00
Hathazari | 235 | 03:00 | 224 | 08:00
Ishurdi | 234 | 08:00 | 223 | 02:00
Jhenaidah | 228 | 07:00 | 211 | 22:00
Kaliakoir | 228 | 18:00 | 220 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 125 | 00:00 | Madartek | 133 | 05:00 | 125 | 00:00
Agargaon | 128 | 06:00 | 122 | 11:00 | Madunaghat | 134 | 18:00 | 126 | 07:00
Agrabad | 135 | 02:00 | 126 | 08:00 | Magura | 129 | 10:00 | 118 | 21:00
AKS | 132 | 02:00 | 125 | 08:00 | Mahasthangarh | 137 | 23:00 | 126 | 21:00
Aminbazar | 128 | 18:00 | 121 | 14:00 | Manikganj | 130 | 18:00 | 122 | 09:00
Amnura | 137 | 18:00 | 121 | 21:00 | Maniknagar | 127 | 18:00 | 121 | 13:00
Ashuganj | 137 | 17:00 | 131 | 13:00 | Matarbari | 119 | 17:00 | 109 | 20:00
Bagerhat | 128 | 09:00 | 112 | 00:00 | Matuail | 129 | 18:00 | 122 | 11:00
Bajitpur | 134 | 17:00 | 122 | 02:00 | Millgate | 132 | 03:00 | 125 | 10:00
Bakulia | 138 | 02:00 | 128 | 06:00 | Mirpur | 127 | 18:00 | 120 | 00:00
Banani | 132 | 06:00 | 123 | 13:00 | Mirzapur | 134 | 18:00 | 127 | 00:00
Bangabhaban | 127 | 06:00 | 122 | 13:00 | Mithapukur | 137 | 23:00 | 124 | 12:00
Barapukuria | 138 | 23:00 | 129 | 12:00 | MI_Cement | 129 | 18:00 | 121 | 11:00
Barguna | 133 | 05:00 | 127 | 02:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 129 | 23:00 | 122 | 01:00 | Mogbazar | 133 | 06:00 | 125 | 00:00
Barishal-230 | 129 | 18:00 | 123 | 00:00 | Mongla | 128 | 09:00 | 114 | 00:00
Baroaulia | 136 | 03:00 | 128 | 08:00 | Motijheel | 127 | 06:00 | 122 | 13:00
Baroirhat | 127 | 18:30 | 118 | 05:00 | Muktagacha | 137 | 18:00 | 124 | 15:00
Bashundhara | 133 | 05:00 | 124 | 12:00 | Munshiganj | 129 | 18:00 | 121 | 10:00
BashundharaCement | 129 | 18:00 | 120 | 11:00 | Muradnagar | 128 | 18:00 | 117 | 13:00
Beanibazar | 132 | 08:00 | 123 | 00:00 | Mymensingh | 138 | 18:00 | 113 | 00:00
Benapole | 123 | 09:00 | 112 | 21:00 | Naogaon | 129 | 14:00 | 123 | 21:00
Bhaluka | 133 | 17:00 | 122 | 13:00 | Narail | 129 | 09:00 | 119 | 21:00
Bhandaria | 123 | 18:30 | 110 | 12:00 | Narinda | 127 | 18:00 | 122 | 13:00
Bhangura | 130 | 02:00 | 126 | 12:00 | Narshingdi | 134 | 17:00 | 115 | 10:00
Bheramara | 137 | 08:00 | 132 | 21:00 | Natore | 132 | 09:00 | 125 | 21:00
Bheramara(GK) | 138 | 09:00 | 131 | 21:00 | Nawabganj | 130 | 18:00 | 123 | 11:00
Bhulta | 121 | 18:30 | 115 | 13:00 | Netrakona | 132 | 17:00 | 111 | 13:00
Bog-Sherpur | 134 | 18:30 | 126 | 21:00 | New | 133 | 23:00 | 126 | 10:00
Bogura | 138 | 07:00 | 130 | 21:00 | Niamatpur | 130 | 02:00 | 126 | 07:00
Bogura-230 | 137 | 15:00 | 130 | 21:00 | Noapara | 128 | 10:00 | 117 | 21:00
Brahmanbaria | 137 | 17:00 | 119 | 00:00 | Pabna | 134 | 09:00 | 127 | 21:00
Cantonment | 128 | 06:00 | 121 | 13:00 | Palashbari | 129 | 00:00 | 122 | 12:00
Chandina | 130 | 18:00 | 121 | 12:00 | Panchagarh | 139 | 05:00 | 120 | 21:00
Chandpur | 135 | 18:30 | 116 | 01:00 | Patuakhali | 134 | 03:00 | 128 | 20:00
Chandraghona | 133 | 02:00 | 126 | 11:00 | Payra | 135 | 18:00 | 132 | 01:00
Chapai | 128 | 19:30 | 122 | 21:00 | PHP | 129 | 18:30 | 116 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:00 | 121 | 11:00 | Postogola | 131 | 18:00 | 122 | 11:00
Chauddagram | 128 | 18:30 | 116 | 11:00 | Purbachal | 133 | 05:00 | 124 | 00:00
Chhatak | 130 | 18:00 | 122 | 00:00 | Purbasadipur | 132 | 23:00 | 119 | 12:00
Chowmuhani | 126 | 18:30 | 109 | 14:00 | Rahanpur | 132 | 18:30 | 128 | 21:00
Chuadanga | 128 | 09:00 | 115 | 21:00 | Rahanpur-400 | 132 | 01:00 | 128 | 21:00
Coxsbazar | 119 | 06:00 | 109 | 20:00 | Rahim | 129 | 18:00 | 123 | 11:00
Cumilla(N) | 130 | 18:00 | 121 | 12:00 | Rajbari | 130 | 08:00 | 123 | 00:00
Cumilla(S) | 132 | 18:00 | 119 | 07:00 | Rajendrapur | 133 | 17:00 | 118 | 13:00
Daudkandi | 127 | 18:00 | 116 | 13:00 | Rajshahi | 133 | 09:00 | 126 | 21:00
Dhaka | 134 | 05:00 | 126 | 00:00 | Rajshahi-230 | 133 | 08:00 | 113 | 13:00
Dhamrai | 134 | 18:00 | 126 | 09:00 | Ramganj | 130 | 18:30 | 108 | 07:00
Dhanmondi | 134 | 05:00 | 125 | 13:00 | Rampur | 135 | 03:00 | 127 | 08:00
Dohazari | 131 | 17:00 | 123 | 08:00 | Rampura | 134 | 05:00 | 124 | 13:00
Faridpur | 132 | 18:30 | 125 | 00:00 | Rangamati | 133 | 18:00 | 125 | 07:00
Fatullah | 131 | 11:00 | 123 | 09:00 | Rangpur | 135 | 23:00 | 123 | 06:00
Fenchuganj | 136 | 17:00 | 129 | 00:00 | Ruppur | 137 | 08:00 | 130 | 21:00
Feni | 128 | 18:30 | 114 | 12:00 | Saidpur | 135 | 23:00 | 123 | 12:00
Ghatail | 135 | 18:00 | 122 | 01:00 | Satkhira | 124 | 09:00 | 112 | 00:00
Ghorashal | 135 | 17:00 | 129 | 00:00 | Satmasjid | 127 | 06:00 | 122 | 00:00
Goalpara | 131 | 09:00 | 121 | 00:00 | Savar | 126 | 18:00 | 120 | 00:00
Gollamari | 131 | 09:00 | 121 | 02:00 | SevenRings | 134 | 17:00 | 127 | 09:00
Gopalganj | 131 | 18:00 | 122 | 01:00 | ShahCement | 130 | 18:00 | 121 | 11:00
Gopalganj-400 | 134 | 18:00 | 128 | 00:00 | Shahjadpur | 137 | 08:00 | 130 | 21:00
Gulshan | 134 | 05:00 | 125 | 13:00 | Shahjibazar | 134 | 16:00 | 121 | 00:00
Halishahar | 138 | 02:00 | 126 | 09:00 | Shahmirpur | 138 | 02:00 | 129 | 07:00
Haripur | 130 | 18:00 | 123 | 10:00 | Shariatpur | 130 | 18:30 | 123 | 00:00
HaripurSBU | 130 | 18:00 | 121 | 08:00 | Sherpur | 140 | 18:00 | 119 | 15:00
Hasnabad | 128 | 05:00 | 122 | 11:00 | Shikalbaha | 125 | 01:00 | 117 | 20:00
Hathazari | 137 | 18:00 | 131 | 09:00 | Shikalbaha-230 | 138 | 02:00 | 130 | 08:00
Ishurdi | 138 | 08:00 | 131 | 21:00 | Shitalakhya | 129 | 18:00 | 121 | 11:00
Jaldhaka | 131 | 01:00 | 119 | 12:00 | Sholosohor | 136 | 02:00 | 125 | 09:00
Jamalpur | 141 | 18:00 | 123 | 19:00 | Shyampur | 131 | 18:00 | 122 | 11:00
Jashore | 128 | 09:00 | 113 | 00:00 | Shyampur-230 | 129 | 18:00 | 122 | 11:00
Jhenaidah | 131 | 09:00 | 121 | 21:00 | Siddhirganj | 129 | 18:00 | 123 | 10:00
Jhenaidah-230 | 130 | 09:00 | 122 | 21:00 | Sirajganj | 133 | 18:30 | 125 | 21:00
Joydebpur | 132 | 17:00 | 120 | 12:00 | Sonargaon | 129 | 18:00 | 121 | 09:00
Joypurhat | 126 | 20:00 | 118 | 12:00 | Sreemongol | 136 | 17:00 | 122 | 00:00
Juldah | 136 | 00:00 | 129 | 07:00 | Sreepur | 133 | 17:00 | 126 | 00:00
Kabirpur | 136 | 12:00 | 122 | 10:00 | Srinagar | 129 | 06:00 | 125 | 13:00
Kachua | 132 | 18:30 | 116 | 14:00 | SSM | 138 | 00:00 | 130 | 21:00
Kaliakoir | 138 | 12:00 | 131 | 08:00 | Sunamganj | 130 | 18:30 | 118 | 00:00
Kallyanpur | 128 | 18:00 | 122 | 09:00 | Sylhet | 132 | 08:00 | 124 | 00:00
Kalurghat | 132 | 03:00 | 126 | 08:00 | Sylhet-132 | 131 | 09:00 | 126 | 00:00
Kamrangirchar | 131 | 18:00 | 123 | 13:00 | Tangail | 132 | 18:00 | 122 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 140 | 05:00 | 124 | 12:00
Kasba | 127 | 18:00 | 117 | 13:00 | TK | 132 | 02:00 | 125 | 12:00
Kazla | 126 | 06:00 | 121 | 13:00 | Tongi | 134 | 23:00 | 128 | 10:00
Keranigonj | 131 | 18:00 | 124 | 11:00 | Ullahpara | 133 | 18:30 | 125 | 21:00
Khagrachori | 132 | 18:00 | 124 | 09:00 | Ullon | 133 | 06:00 | 124 | 13:00
Khulna | 130 | 10:00 | 119 | 00:00 | Uttara | 125 | 18:00 | 119 | 11:00
Khulna(S) | 131 | 09:00 | 121 | 00:00 | UttaraNew | 126 | 18:00 | 120 | 11:00
Khulshi | 133 | 01:00 | 126 | 11:00 | Zigatola | 131 | 18:00 | 124 | 11:00
Kishoreganj | 133 | 16:00 | 118 | 00:00
Kodda | 134 | 12:00 | 121 | 13:00
KSRM | 135 | 18:00 | 128 | 07:00
Kulaura | 136 | 19:00 | 128 | 00:00
Kurigram | 135 | 22:00 | 122 | 07:00
Kushtia | 134 | 09:00 | 126 | 21:00
Lalbag | 130 | 18:00 | 123 | 11:00
Lalmonirhat | 132 | 23:00 | 120 | 12:00
Madanganj | 129 | 18:00 | 120 | 11:00
Madaripur | 132 | 18:00 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division